VRI

Environmental Services

VILLAGE OF MEDINA WWTF DISCHARGE QUALITY – March 2007

VRI

- Environmental Services

Village Board

Village of Medina

600 Main Street

Medina, New York 14103

Re: Wastewater Treatment Plant – Facilities Operation Report.

The Village’s Facility treated on average 3,020,000 gallons per day in March 2007. New York State Discharge Permit {NYS-SPDES} limits were met over the period. Below are the projects completed and other significant notes. Daily operations/maintenance activities conducted as scheduled.

- Projects and significant events of record.

- Composting operation processed 0 tons of belt filter pressed sludge.

- 7.5916 tons sludge land filled due to Auggie truck being broken down.

- Removed 26 cubic feet of grit from influent.

- Greased all equipment.

- Weekly checks of overflow points conducted.

- Thawed secondary airlift.

- Pumped sludge out of secondary and drained.

- Pulled Ferric pump serviced and reinstalled.

- Replaced one probe at compost building.

- Had to unplug east thickner line several times.

- Pulled belt press apart and cleaned.

- Power outage on 26PthP. Had to reset controls for facility operations.

- D.P.W excavated and repaired airline leak in driveway.

Steven C. Stauffer

Regional Manager

Valley River Inc.